## Sheet3
Head and Power Loss Calculator For Water Flow
Data Required
Flow Rate | 10 | m3/hr
Pipe Dia | 50 | mm
Total Length | 1 | m
Surface Roughness | 0.003 | mm
Results
Velocity | 1.4154 | m/s
Reynolds Number | 70630.1481
Friction Factor | 0.017515
Loss In Terms of Pressure | 0.0035089 | bar
Loss in Terms of Head | 0.035089 | m
Pumping Power Required | 0.9747 | Watt

## Sheet1 (hidden)
Flow Rate | 10 | m3/hr | 0.0027778 | m3/s
Pipe Dia | 50 | mm | 0.05
Total Length | 1 | m
Surface Roughness | 0.003 | mm
Cross Sectional Area | 0.0019625 | m2
Velocity | 1.4154 | m/s |  |  | e/d | 6e-05
Re | 70630.1481 |  |  |  | f | 0.017515
[5 empty] | root f | 0.13234
F for Leminar | 0.00022653 |  |  |  | eq | 0.46504
F for Turbulent | 0.017515
F final | 0.017515
pressure loss | 0.0035089 | bar
head loss | 0.035089
Power Required | 0.9747 | W