## Sheet2
Saturated Steam Velocity in Pipes
Input
Pressure | 5 | bar
Flow Rate | 1000 | kg/hr
Pipe Diameter | 65 | mm
Result
Velocity | 26.4 | m/s
Remarks: Velocity should be in the range of 30 m/s to 40m/s for saturated steam

## Steam table (hidden)
| Pressure |  | Temperature | Specific Enthalpy |  |  | Specific
|  |  | oC |  |  |  | Volume Steam m3/kg
bar |  | kPa |  | Water (hf) kJ/kg | Evaporation (hfg ) kJ/kg | Steam (hg ) kJ/kg |  | Boiler Working Pressure |  |  | Vs |  | Vs
[8 empty] | 5 | 4.5 | 0.342 | 0.315 | 0.342 | 0.315
[9 empty] | 5 | 0.315 |  | 0.315 |  | 5
1000
65
0 |  | 0 | 100 | 419.04 | 2257 | 2676 | 1.673 | [5 empty] | Ac | 0.0033166 | m2
0.1 |  | 10 | 102.66 | 430.2 | 2250.2 | 2680.2 | 1.533 | [5 empty] | v | 26.4 | m/s
0.2 |  | 20 | 105.1 | 440.8 | 2243.4 | 2684.2 | 1.414
0.3 |  | 30 | 107.39 | 450.4 | 2237.2 | 2687.6 | 1.312
0.4 |  | 40 | 109.55 | 459.7 | 2231.3 | 2691 | 1.225
0.5 |  | 50 | 111.61 | 468.3 | 2225.6 | 2693.9 | 1.149
0.6 |  | 60 | 113.56 | 476.4 | 2220.4 | 2696.8 | 1.083
0.7 |  | 70 | 115.4 | 484.1 | 2215.4 | 2699.5 | 1.024
0.8 |  | 80 | 117.14 | 491.6 | 2210.5 | 2702.1 | 0.971
0.9 |  | 90 | 118.8 | 498.9 | 2205.6 | 2704.5 | 0.923
1 |  | 100 | 120.42 | 505.6 | 2201.1 | 2706.7 | 0.881
1.1 |  | 110 | 121.96 | 512.2 | 2197 | 2709.2 | 0.841
1.2 |  | 120 | 123.46 | 518.7 | 2192.8 | 2711.5 | 0.806
1.3 |  | 130 | 124.9 | 524.6 | 2188.7 | 2713.3 | 0.773
1.4 |  | 140 | 126.28 | 530.5 | 2184.8 | 2715.3 | 0.743
1.5 |  | 150 | 127.62 | 536.1 | 2181 | 2717.1 | 0.714
1.6 |  | 160 | 128.89 | 541.6 | 2177.3 | 2718.9 | 0.689
1.7 |  | 170 | 130.13 | 547.1 | 2173.7 | 2720.8 | 0.665
1.8 |  | 180 | 131.37 | 552.3 | 2170.1 | 2722.4 | 0.643
1.9 |  | 190 | 132.54 | 557.3 | 2166.7 | 2724 | 0.622
2 |  | 200 | 133.69 | 562.2 | 2163.3 | 2725.5 | 0.603
2.2 |  | 220 | 135.88 | 571.7 | 2156.9 | 2728.6 | 0.568
2.4 |  | 240 | 138.01 | 580.7 | 2150.7 | 2731.4 | 0.536
2.6 |  | 260 | 140 | 589.2 | 2144.7 | 2733.9 | 0.509
2.8 |  | 280 | 141.92 | 597.4 | 2139 | 2736.4 | 0.483
3 |  | 300 | 143.75 | 605.3 | 2133.4 | 2738.7 | 0.461
3.2 |  | 320 | 145.46 | 612.9 | 2128.1 | 2741 | 0.44
3.4 |  | 340 | 147.2 | 620 | 2122.9 | 2742.9 | 0.422
3.6 |  | 360 | 148.84 | 627.1 | 2117.8 | 2744.9 | 0.405
3.8 |  | 380 | 150.44 | 634 | 2112.9 | 2746.9 | 0.389
4 |  | 400 | 151.96 | 640.7 | 2108.1 | 2748.8 | 0.374
4.5 |  | 450 | 155.55 | 656.3 | 2096.7 | 2753 | 0.342
5 |  | 500 | 158.92 | 670.9 | 2086 | 2756.9 | 0.315
5.5 |  | 550 | 162.08 | 684.6 | 2075.7 | 2760.3 | 0.292
6 |  | 600 | 165.04 | 697.5 | 2066 | 2763.5 | 0.272
6.5 |  | 650 | 167.83 | 709.7 | 2056.8 | 2766.5 | 0.255
7 |  | 700 | 170.5 | 721.4 | 2047.7 | 2769.1 | 0.24
7.5 |  | 750 | 173.02 | 732.5 | 2039.2 | 2771.7 | 0.227
8 |  | 800 | 175.43 | 743.1 | 2030.9 | 2774 | 0.215
8.5 |  | 850 | 177.75 | 753.3 | 2022.9 | 2776.2 | 0.204
9 |  | 900 | 179.97 | 763 | 2015.1 | 2778.1 | 0.194
9.5 |  | 950 | 182.1 | 772.5 | 2007.5 | 2780 | 0.185
10 |  | 1000 | 184.13 | 781.6 | 2000.1 | 2781.7 | 0.177
10.5 |  | 1050 | 186.05 | 790.1 | 1993 | 2783.3 | 0.171
11 |  | 1100 | 188.02 | 798.8 | 1986 | 2784.8 | 0.163
11.5 | 1150 |  | 189.82 | 807.1 | 1979.1 | 2786.3 | 0.157
12 | 1200 |  | 191.68 | 815.1 | 1972.5 | 2787.6 | 0.151
12.5 | 1250 |  | 193.43 | 822.9 | 1965.4 | 2788.8 | 0.146
13 | 1300 |  | 195.1 | 830.4 | 1959.6 | 2790 | 0.141
13.5 | 1350 |  | 196.62 | 837.9 | 1953.2 | 2791.1 | 0.136
14 | 1400 |  | 198.35 | 845.1 | 1947.1 | 2792.2 | 0.132
14.5 | 1450 |  | 199.92 | 852.1 | 1941 | 2793.1 | 0.128
15 | 1500 |  | 201.45 | 859 | 1935 | 2794 | 0.124
15.5 | 1550 |  | 202.92 | 865.7 | 1928.8 | 2794.9 | 0.119
16 | 1600 |  | 204.38 | 872.3 | 1923.4 | 2795.7 | 0.117
17 | 1700 |  | 207.17 | 885 | 1912.1 | 2797.1 | 0.11
18 | 1800 |  | 209.9 | 897.2 | 1901.3 | 2798.5 | 0.105
19 | 1900 |  | 212.47 | 909 | 1890.5 | 2799.5 | 0.1
20 | 2000 |  | 214.96 | 920.3 | 1880.2 | 2800.5 | 0.0949
21 | 2100 |  | 217.35 | 931.3 | 1870.1 | 2801.4 | 0.0906
22 | 2200 |  | 219.65 | 941.9 | 1860.1 | 2802 | 0.0868
23 | 2300 |  | 221.85 | 952.2 | 1850.4 | 2802.6 | 0.0832
24 | 2400 |  | 224.02 | 962.2 | 1840.9 | 2803.1 | 0.0797
25 | 2500 |  | 226.12 | 972.1 | 1831.4 | 2803.5 | 0.0768
26 | 2600 |  | 228.15 | 981.6 | 1822.2 | 2803.8 | 0.074
27 | 2700 |  | 230.14 | 990.7 | 1813.3 | 2804 | 0.0714
28 | 2800 |  | 232.05 | 999.7 | 1804.4 | 2804.1 | 0.0689
29 | 2900 |  | 233.93 | 1008.6 | 1795.6 | 2804.2 | 0.0666
30 | 3000 |  | 235.78 | 1017 | 1787 | 2804.1 | 0.0645
31 | 3100 |  | 237.55 | 1025.6 | 1778.5 | 2804.1 | 0.0625
32 | 3200 |  | 239.28 | 1033.9 | 1770 | 2803.9 | 0.0605
33 | 3300 |  | 240.97 | 1041.9 | 1761.8 | 2803.7 | 0.0587
34 | 3400 |  | 242.63 | 1049.7 | 1753.8 | 2805.5 | 0.0571
35 | 3500 |  | 244.26 | 1057.7 | 1745.5 | 2803.2 | 0.0554
36 | 3600 |  | 245.86 | 1065.7 | 1737.2 | 2802.9 | 0.0539
37 | 3700 |  | 247.42 | 1072.9 | 1729.5 | 2802.4 | 0.0524
38 | 3800 |  | 248.95 | 1080.3 | 1721.6 | 2801.9 | 0.051
39 | 3900 |  | 250.42 | 1087.4 | 1714.1 | 2801.5 | 0.0498
40 | 4000 |  | 251.94 | 1094.6 | 1706.3 | 2800.9 | 0.0485
41 | 4100 |  | 253.34 | 1101.6 | 1698.3 | 2799.9 | 0.0473
42 | 4200 |  | 254.74 | 1108.6 | 1691.2 | 2799.8 | 0.0461
43 | 4300 |  | 256.12 | 1115.4 | 1683.7 | 2799.1 | 0.0451
44 | 4400 |  | 257.5 | 1122.1 | 1676.2 | 2798.3 | 0.0441
45 | 4500 |  | 258.82 | 1228.7 | 1668.9 | 2797.6 | 0.0431
46 | 4600 |  | 260.13 | 1135.3 | 1666.6 | 2796.9 | 0.0421
47 | 4700 |  | 261.43 | 1142.2 | 1654.4 | 2796.6 | 0.0412
48 | 4800 |  | 262.73 | 1148.1 | 1647.1 | 2795.2 | 0.0403
49 | 4900 |  | 264 | 1154.5 | 1639.9 | 2794.4 | 0.0394
50 | 5000 |  | 265.26 | 1160.8 | 1632.8 | 2793.6 | 0.0386
51 | 5100 |  | 266.45 | 1166.6 | 1626.9 | 2792.6 | 0.0378
52 | 5200 |  | 267.67 | 1172.6 | 1619 | 2791.6 | 0.0371
53 | 5300 |  | 268.84 | 1178.7 | 1612 | 2790.7 | 0.0364
54 | 5400 |  | 270.02 | 1184.6 | 1605.1 | 2789.7 | 0.0357
55 | 5500 |  | 271.2 | 1190.5 | 1598.2 | 2788.7 | 0.035
56 | 5600 |  | 272.33 | 1196.3 | 1591.3 | 2787.6 | 0.0343
57 | 5700 | 273.45 | 1202.1 |  | 1584.5 | 2786.6 | 0.0337
58 | 5800 | 274.55 | 1207.8 |  | 1577.7 | 2785.5 | 0.0331
59 | 5900 | 275.65 | 1213.4 |  | 1571 | 2784.4 | 0.0325
60 | 6000 | 276.73 | 1218.9 |  | 1564.4 | 2783.3 | 0.0319
61 | 6100 | 277.8 | 1224.5 |  | 1557.6 | 2782.1 | 0.0314
62 | 6200 | 278.85 | 1230 |  | 1550.9 | 2780.9 | 0.0308
63 | 6300 | 279.89 | 1235.4 |  | 1544.3 | 2779.7 | 0.0303
64 | 6400 | 280.92 | 1240.8 |  | 1537.3 | 2778.5 | 0.0298
65 | 6500 | 281.95 | 1246.1 |  | 1531.2 | 2777.3 | 0.0293
66 | 6600 | 282.95 | 1251.4 |  | 1524.7 | 2776.1 | 0.0288
67 | 6700 | 283.95 | 1256.7 |  | 1518.1 | 2774.8 | 0.0283
68 | 6800 | 284.93 | 1261.9 |  | 1511.6 | 2773.5 | 0.0278
69 | 6900 | 285.9 | 1267 |  | 1501.1 | 2772.1 | 0.0274
70 | 7000 | 286.85 | 1272.1 |  | 1498.7 | 2770.8 | 0.027
71 | 7100 | 287.8 | 1277.3 |  | 1492.2 | 2769.5 | 0.0266
72 | 7200 | 288.75 | 1282.3 |  | 1485.8 | 2768.1 | 0.0262
73 | 7300 | 289.69 | 1287.3 |  | 1479.4 | 2766.7 | 0.0258
74 | 7400 | 290.6 | 1292.3 |  | 1473 | 2765.3 | 0.0254
75 | 7500 | 291.51 | 1297.2 |  | 1466.6 | 2763.8 | 0.025
76 | 7600 | 292.41 | 1302.3 |  | 1460.2 | 2762.5 | 0.0246
77 | 7700 | 293.91 | 1307 |  | 1453.9 | 2760.9 | 0.0242
78 | 7800 | 294.2 | 1311.9 |  | 1447.6 | 2759.5 | 0.0239
79 | 7900 | 295.1 | 1316.7 |  | 1441.3 | 2758 | 0.0236
80 | 8000 | 295.96 | 1321.5 |  | 1435 | 2756.5 | 0.0233
81 | 8100 | 296.81 | 1326.2 |  | 1428.7 | 2754.9 | 0.0229
82 | 8200 | 297.66 | 1330.9 |  | 1422.5 | 2753.4 | 0.0226
83 | 8300 | 298.5 | 1335.7 |  | 1416.2 | 2751.9 | 0.0223
84 | 8400 | 299.35 | 1340.3 |  | 1410 | 2750.3 | 0.022
85 | 8500 | 300.2 | 1345 |  | 1403.8 | 2748.8 | 0.0217
86 | 8600 | 301 | 1349.6 |  | 1397.6 | 2747.2 | 0.0214
87 | 8700 | 301.81 | 1354.2 |  | 1391.3 | 2745.5 | 0.0211
88 | 8800 | 302.61 | 1358.8 |  | 1385.2 | 2744 | 0.0208
89 | 8900 | 303.41 | 1363.3 |  | 1379 | 2742.3 | 0.0205
90 | 9000 | 304.2 | 1367.8 |  | 1372.7 | 2740.5 | 0.0202
92 | 9200 | 305.77 | 1376.8 |  | 1360.3 | 2737.1 | 0.0197
94 | 9400 | 307.24 | 1385.7 |  | 1348 | 2733.7 | 0.0192
96 | 9600 | 308.83 | 1394.5 |  | 1335.7 | 2730.2 | 0.0187
98 | 9800 | 310.32 | 1403.2 |  | 1323.3 | 2726.5 | 0.0183
100 | 10000 | 311.79 | 1411.9 |  | 1310.9 | 2722.8 | 0.0178
102 | 10200 | 313.24 | 1420.5 |  | 1298.7 | 2719.2 | 0.0174
104 | 10400 | 314.67 | 1429 |  | 1286.3 | 2715.3 | 0.017
106 | 10600 | 316.08 | 1437.5 |  | 1274 | 2711.5 | 0.0166
108 | 10800 | 317.46 | 1445.9 |  | 1261.7 | 2707.6 | 0.0162
110 | 11000 | 318.83 | 1454.3 |  | 1249.3 | 2703.6 | 0.0158
112 | 11200 | 320.17 | 1462.6 |  | 1237 | 2699.6 | 0.0154
114 | 11400 | 321.5 | 1470.8 |  | 1224.6 | 2695.4 | 0.015
116 | 11600 | 322.81 | 1479 |  | 1212.2 | 2691.2 | 0.0147
118 | 11800 | 324.1 | 1487.2 |  | 1199.8 | 2687 | 0.0144
120 | 12000 | 325.38 | 1495.4 |  | 1187.3 | 2682.7 | 0.0141